SECTION 08 33 44

Overhead coiling Fire curtains

1. GENERAL
   1. Section Includes
      1. Fire- and Smoke-Protective Curtain Assemblies for Large Openings.
      2. Fire- and Smoke-Protective Curtain Assemblies with Egress.
   2. Related Sections

[Specifier Notes]: Remove sections not required under project scope of work.

* + 1. Section 08 33 43 – Overhead Coiling Smoke Curtains.
    2. Section 28 30 00 – Detection and Alarms.
  1. Administrative Requirements
     1. Coordination:
        1. Coordinate with Owner or Owner’s representative regarding network configuration and estimated throughput utilization prior to performing network connections.
     2. Sequencing / Scheduling: Provide to Owner or Owner’s representative a schedule and list of participants required to attend coordination and progress update meetings.

[Specifier Notes] – Retain only those individuals required to be in attendance for progress meetings. Delete the entire following sub-paragraph if not required.

* + - 1. Owner representative(s).
      2. General Contractor.
      3. Project Manager.
      4. Manufacturer’s Representative.
      5. Project Architect.
      6. Project Engineer.
  1. Coordination
     1. Coordinate fire and smoke curtain assemblies with power, signal, fire-alarm, and smoke-detection systems specified in Division 26 and Division 28.
     2. Coordinate fire- and smoke-protective curtain assemblies with ceilings for operational clearances and maintenance access requirements.
     3. Coordinate fire- and smoke-protective curtain assemblies with walls for support requirements, rating continuity above ceilings, and recessed wall switches.
     4. Coordinate requirements for metal supports required for fire- and smoke-protective curtain assemblies.
  2. Informational Submittals
     1. Submit under provisions of Section 01 30 00.
     2. Product Data: Manufacturer's product information and data sheets for each product specified in this section, including:
        1. Substrate preparation instructions and recommendations
        2. Installation means and methods.
        3. Recommendations and requirements for proper storage and handling.
     3. Shop Drawings:
        1. Submit Manufacturer’s approved shop drawings detailing the section and elevation views of each product to be installed.
        2. Coordinate with locations listed on Contract Drawings.
     4. Warranty Information:
        1. Submit confirmation and details of manufacturer’s warranty, extended warranty, and replacement policies.
  3. Closeout SUBMITTALS
     1. Operation and Maintenance Data: For smoke- and fire-protective curtain assemblies to include in emergency, operation, and maintenance manuals.
     2. Field quality-control reports for required testing.
  4. QUALITY ASSURANCE
     1. Qualifications:
        1. Manufacturer: Minimum of seven (7) years experience in manufacturing fire-and-smoke-protective curtain assemblies at a facility in the United States that have been successfully installed in compliance with requirements of authorities having jurisdiction.
        2. Installers: An entity that employs installers and supervisors who are trained and approved by manufacturer for both installation and maintenance of units required for this Project.
  5. Delivery, Storage and Handling
     1. Deliver, store and handle materials and products in accordance with the manufacturer's instructions and recommendations and industry standards.
     2. Store all materials in the manufacturer’s original packaging until ready for installation. Protect all products from damage or exposure to adverse weather conditions.
  6. Project Conditions
     1. Prior to fabrication, verify that dimensions are consistent with those found in the construction drawings. Where discrepancies exist, confirm the proper dimensions with the Architect before proceeding with work.
  7. WARRANTY
     1. Manufacturer Warranty: Provide manufacturer’s warranty covering parts and labor costs to repair or replace part that fail to perform.
        1. Warranty Period: Parts and labor warranty for 12 months from date of Substantial Completion or date of purchase, whichever comes first.

1. Products

* 1. MANUFACTURERS

[Specifier Notes] – Retain the following Paragraph if this document is a PROPRIETARY Specification, with Avigilon’s products listed as the Basis of Design. Delete if not required.

* + 1. Basis of Design Manufacturer: Smoke Guard, A CSW Industrials Company.
       1. Address: 287 N. Maple Grove, Boise, ID 83704.
       2. Phone: (800) 574-0330.
       3. Website: https://smokeguard.com

[Specifier Notes] – Retain the following Paragraph if this document is written as a PERFORMANCE specification, without listing a manufacturer as a basis of design. Insert manufacturers that sell products comparable to those specified in this section. Delete if not required.

* + 1. Manufacturer List:
       1. Manufacturer:
    2. Substitution Limitations:
       1. Submit substitution requests in accordance with provisions of Section 01 60 00.
       2. Single manufacturer will provide, from a single source, a fully integrated smoke-and-draft containment system consisting of fire-and-smoke-protective curtains and the following components:

[Specifier Notes] – From the following paragraphs, retain only those defined under the scope of work for this project.

* + - * 1. Fire-and-Smoke-Protective Curtain Operators.
        2. Fire-and-Smoke-Protective Curtain Controls.
  1. PERFORMANCE REQUIREMENTS

[Specifier Notes] – Retain "Fire-Protective Curtain Assemblies" Paragraph below if applicable. Overhead coiling curtains are labeled by UL for sizes not exceeding 152 sq. ft. (14 sq. m), with no dimension exceeding 13 feet, 6 inches (4.11 m).

* + 1. Fire-Protective Curtain Assemblies: Complying with NFPA 80; listed and labeled by qualified testing agency, for fire-protection ratings indicated, based on testing at as close to neutral pressure as possible in accordance with UL 10D.
       1. Oversize Rated Curtain Assemblies: For units exceeding sizes of tested assemblies, provide certification by a qualified testing agency that curtain assemblies comply with standard construction requirements for tested and labeled fire-rated curtain assemblies, except for size.
       2. Fire-Resistance Ratings: Comply with the following; testing by a qualified testing agency. Identify products with appropriate markings of applicable testing agency.
          1. NFPA 252 Rating: 20 minutes.
          2. UL 10B Rating: 20 minutes.
          3. UL 10C Rating: 20 minutes (without hose stream test).
          4. UL 10D Rating: 2 hours.
    2. Smoke Control: Provide smoke- and fire-protective curtain assemblies that are listed and labeled with the letter "S" on the rating label by a qualified testing agency for smoke- and draft-control based on testing in accordance with UL 1784 without an artificial bottom seal; with maximum air-leakage rate of 3.0 cfm/sq. ft. (0.01524 cu. m/s x sq. m) of opening at 0.10 inch wg (24.9 Pa) for both ambient and elevated temperature tests.
    3. Curtain Materials: Provide manufacturer’s standard multi-layer glass fiber fabric coated on one or both sides complying with each of the following:
       1. Fire-Test-Response Characteristics: Provide products that pass NFPA 701, as determined by testing of fabrics that were treated using treatment-application method intended for use for this Project by a testing and inspecting agency acceptable to authorities having jurisdiction.
       2. Flame-Spread and Smoke-Developed Indexes: 25 and 450, respectively, when tested in accordance with ASTM E84.
    4. Curtain Attachment: Curtain shall form a pressure-resisting seal with
       1. Side Guides: Formed from galvanized-steel sheet conforming to ASTM A653/A653M with integral pressure-retaining tabs.
       2. Weighted Bottom Bar: Provide weighted bottom bar to ensure smooth operation and hold curtain taut.
    5. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.
    6. Housing Type: Sheet metal housings containing support rollers and associated electronics.
       1. Coordinate operator wiring requirements and electrical characteristics with building electrical system.
    7. Operation: Controlled descent automatically by fail-safe gravity deployment and motorized rewind. Curtain deploys on activation of one of the following:

[Specifier Notes] – Retain subparagraphs one and three. Retain subparagraph two to suit Project.

* + - 1. Local Smoke Detector.
      2. Building Fire Alarm.
      3. Testing Key Switch.
    1. Release Mechanism: Labelled as defined by UL864.
  1. Fire- and SMOKE-PROTECTIVE CURTAIN ASSEMBLIES for large openings
     1. Alarm-activated fabric fire and smoke curtain assembly complying with NFPA 92.

[Specifier Notes] – Retain the following Paragraph if the specification is meant to be proprietary to Smoke Guard products. Delete if a performance-based specification is required.

* + - 1. Basis of Design Product: Model 2500 Fire + Smoke, by Smoke Guard, a CSW Industrials Company.
      2. Minimum Opening Size: 6 feet by 1 foot 6 inches (1.83 by 0.46m).
      3. Maximum Opening Size:

[Specifier Notes] – Retain at least one of the following subparagraphs to suit Project.

* + - * 1. Up to 40 by 20 feet (12.19 by 6.10m).
        2. Up to 50 by 16 feet (15.24 by 4.88m).
        3. Up to 60 by 12 feet (18.29 by 3.66m).
  1. Fire- and SMOKE-PROTECTIVE CURTAIN ASSEMBLIES with EGress
     1. Alarm-activated fabric fire and smoke curtain assembly complying with NFPA 92.

[Specifier Notes] – Retain one of the following Paragraph if the specification is meant to be proprietary to Smoke Guard products. Delete if a performance-based specification is required.

* + - 1. Basis of Design Product: Model 2500 Egress, by Smoke Guard, a CSW Industrials Company.
      2. Minimum Opening Size: 6 feet 6 inches by 8 feet (1.98 by 2.44m).
      3. Maximum Opening Size: 15 feet by 20 feet (4.57 by 6.10m).
      4. Integrated Egress Opening: Manufacturer's standard swinging fabric flap with overlapping design to maintain fire and smoke rating.
         1. Provide curtain with readily operable egress flap from egress side without use of keys, tools, or special knowledge in compliance with opening force requirements of authorities having jurisdiction.
         2. Provide curtain allowing push through manual egress with less than 15 pounds release pressure in the direction of travel.

1. EXECUTION
   1. EXAMINATION
      1. Examine substrates upon which work will be installed.
         1. Verify related work performed under other sections is complete and in accordance with Shop Drawings.
         2. Verify wall surfaces and elevator door frames are acceptable for installation of smoke containment system components.
      2. Coordinate with responsible entity to perform corrective work on unsatisfactory substrates.
      3. Proceed with installation only after unsatisfactory conditions have been corrected.
      4. Verify that locations of concealed reinforcements have been clearly marked for the installer.
      5. Locate reinforcement points and clearly mark their locations if not already done.
   2. PREPARATION
      1. Clean surfaces prior to installation.
      2. Prepare surfaces as recommended by the manufacturer for achieving optimal results.
   3. INSTALLATION
      1. Install in accordance with manufacturer’s current installation instructions and industry recognized best practices.
      2. Install in accordance with all code bodies having jurisdiction.
   4. Cleaning and Protection
      1. Clean and remove all stains, grime, or other soils using soap and water. Only use detergents approved by the manufacturer for use on the finishes specified. Do not use acid solutions, steel wool, and other harsh abrasives.
      2. Damaged products must be repaired or replaced prior to substantial completion.
      3. Protect installed products until completion of work specified in this section.
   5. FIELD QUALITY CONTROL
      1. Field Test: Follow manufacturer’s cycle test procedures.
         1. Notify Owner’s Representative, local Fire Marshal, alarm sub-contractor and elevator sub-contractor or service company minimum one week in advance of scheduled testing.
         2. Complete maintenance service record.
   6. DEMONSTRATION
      1. Demonstrate required testing and maintenance procedures to Owner’s Representative.
   7. Maintenance and Testing:
      1. Perform minimum semi-annual maintenance and testing on each smoke containment system as required by the manufacturer’s warranty, code agency evaluation reports, and as required by local authority having jurisdiction.
         1. Retain permanent record of tests.
      2. Fire Event: Owner shall engage a qualified inspector to assess unit(s) after exposure to a fire event.

END OF SECTION