Section 08 3494

AUTOMATIC HORIZONTAL coiling fabric Fire Curtain

# General

## Summary

### Section Includes:

#### Smoke detector-activated, ceiling mounted, horizontal coiling fabric fire curtain.

#### Self-closing UL864 listed controller by ETL.

#### For ceiling application at horizontal protected openings.

### Related Requirements:

#### 08 3100Access Panels.

#### 09 2200 Load Bearing Header Framing

#### 09 9100Paint: Field painting of specified components.

#### 28 3000Detection and Alarm: Provision of fire alarm.

#### Division 26 Sections for 120V and control circuit power including conduit, boxes, conductors, wiring devices, and emergency power.

## References

### NFPA Codes and Standards:

#### 70  National Electrical Code.

#### 72 – National Fire Alarm Code

### UL Standards:

#### 268  Smoke Detectors for Fire Protective Signaling Systems.

#### 864  Control Units for Fire Protective Signaling Systems.

## SUSTAINABLE DESIGN REQUIREMENTS

### LEED-NC: Comply with Section 01 8100 Sustainable Design Requirements including, without limitation, submittal and documentation requirements.

### Credit/Point Goals Applicable To This Section: In addition to global Project credit/point goals:

#### Materials & Resources - Construction Waste Management

#### Materials & Resources - Recycled Content

#### Materials & Resources - Regional Materials

#### Indoor Environmental Quality - Construction IAQ Management Plan

## submittals

### Comply with Section 01 3300Submittal Procedures:

#### Product Data.

#### Shop Drawings:

##### Include opening dimensions.

##### Show and identify related work performed under other sections of the specifications.

#### Quality Assurance/Control Submittals:

##### Certifications.

##### Manufacturer’s installation instructions and testing procedures.

## closeout submittals

### Comply with Section 01 7700Project Closeout:

#### Operation and Maintenance Manual.

#### Manufacturer’s Warranty

## Quality Assurance

### Certifications:

#### ETL listed per UL864

#### Intertek listed per UL10D

### Pre-Installation Meeting:

#### Schedule and convene a pre-installation meeting prior to commencement of field operations with representatives of the following in attendance: Owner, Architect, General Contractor, fire barrier system sub-contractor, and electrical sub-contractor.

#### Review substrate conditions, requirements of related work, installation instructions, storage and handling procedures, and protection measures.

#### Document responsibilities of various parties and deviations from specifications and installation instructions.

## Delivery, Storage, and Handling

### Comply with Section 01 6600Delivery, Storage, and Handling.

### Comply with manufacturer’s instructions.

## Warranty

### Provide manufacturer’s standard one year warranty.

### Maintenance and Testing:

#### Perform minimum annual maintenance and testing on each as required by the manufacturer’s warranty, code agency evaluation reports, and as required by local authority having jurisdiction.

#### Backup Battery: Tested per the Operation and Maintenance Manual.

#### Provide test documentation.

# Products

## ManufactureD units

### Manufacturer:

#### Smoke Guard, 287 Maple Grove, Boise, Idaho  83704  www.smokeguard.com

### Label each fire curtain system with following information:

#### Manufacturer’s name.

#### Label of quality control agency.

## Performance / DESIGN CRITERIA

### Test Operation and Fire Operation: controlled by building fire alarm system signal and test switch.

#### Curtain after Test and After Fire Alarm: Power operated motor in roller.

#### After Test and After Fire Alarm: Automatic. No service call needed. No replacement parts needed.

## Components

### Curtain Fabric:  Glass filament fabrics of glass fiber material coated on one side.

#### SG TEX 30

#### Rating:  2 hours.

### Side Guide Assembly:  Manufacturer’s standard.

### Leading Edge:  Manufacturer’s standard.

### Control System:

#### ETL listed to UL 864.

#### With battery backup.

### Finishes:

#### Galvanized, field finished as noted.

## fabrication

### Installation Configuration:  Housing attached directly to ceiling above opening.

### Fabricate and install mounting brackets, hardware, and fasteners needed to attach curtain assembly to building structure.

# Execution

## Examination

### Examine substrates to which work will be installed.

#### Verify related work performed under other sections is complete and in accordance with Shop Drawings.

#### Verify wall surfaces are acceptable for installation of smoke containment system components.

### Coordinate with responsible entity to perform corrective work on unsatisfactory substrates.

### Coordinate electrical interface and connection with Division 26.

### Coordinate interface and connection with fire alarm system.

### Commencement of work by installer is acceptance of substrate.

## INSTALLATION

### Install fire curtain system components in accordance with manufacturer’s installation instructions.

## Field Quality Control

### Field Test: Follow manufacturer’s cycle test procedures.

#### Notify Owner’s Representative, local Fire Marshal and alarm sub-contractor minimum one week in advance of scheduled testing.

#### Complete maintenance service record.

## Demonstration

### Demonstrate required testing and maintenance procedures to Owner’s Representative.

End of Section